## IBAL
Date | Issue | Solution
2022-01-11 | IBAL: Emulation at the startup period is not responsive enough. | Controller has been turned to be more aggressive.
2022-01-21 | IBAL: In humid season, relative humidity of the internal zone is 100% at the startup, which seems unreasonable. It also makes latent load emulation difficult and puts significant latent load on AHU2 during the startup. | The day before the selected test day is added into the EnergyPlus simulation. The simulation of this day is handeled internally by callSim. During the simulation of this day, 10kg/s 80F 50% air is supplied to all the emulated zone, which results in initial zone air with similar condition.
2022-02-07 | IBAL: large latent load emulation erros, about 500-600W | Use humidity ratio instead of relative humidity for humidity control
2022-02-09 | IBAL: VFD issue | VFD replaced (2/15)
2022-02-24 | Power bump during the night took the chiller offline | Reset the chiller, but lost the test
2022-02-25 | Power bump during the afternoon took the chiller offline | Reset the chiller, but lost the test
2022-03-06 | Target computer was corrupted | Reformat the harddisk and manually reset the system (3/7)
2022-03-15 | AHU2 fan overcurrent fault | Not sure on the long term fix, but short term increased the acceleration and decelerration times.
2022-03-18 | AHU2 fan overcurrent fault - lost the test at the end
2022-03-19 | AHU2 fan overcurrent fault
2022-03-23 | AHU2 fan overcurrent fault during a test. The fan reset and the test finished, but for the period of time it was off the sensible load in Zone2 was off.
2022-03-24 | AHU2 fan overcurrent fault and then an Earth fault. | Ordered a new VFD. Continuing to troubleshoot and figuring out a design to provide more cooling in the VFD cabinet. Re-did some wiring in the motor that seemed to be flaky.
2022-03-30 | Leak in Chiller1 | 3/31/2022 - found a crack in the suction pipe to the compressor. Brazed over the crack. Likely caused by vibrations.
4/8/2022-4/19/2022 | NIST site wide utility outage from 5 pm April 8 through 11 pm April 10. No chilled water or steam available during that time, so no testing can be conducted.
2022-04-05 | Leak in Chiller1 | Ground off prior repair and brazed over the crack again, this time while pulling a vacuum on the line to ensure that there was no pressure to blow the solder out of the crack.
2022-04-11 | Compressor freeze fault during a test | Reset the chiller and monitor the performance to see if this was just a one time error or a symptom of something. Update 4/12/2022: I watched the chiller when it ran into this issue and it looks like this is a case where Chiller1 is just overloaded and I need to modify the code to switch to Chiller2.
2022-04-18 | Leak in Chiller1 | Second repair didn't hold. Replaced compressor and charged chiller on 4/21/2022.
2022-05-06 | AHU2 fan faulted | 5/9/2022 - replaced all wiring at the motor. Only time will tell if that was effective.
2022-05-24 | AHU2 fan faulted | 5/24/2022 - replaced VFD; still troubleshooting. 5/25-26/2022 - replaced wiring running from the disconnect to the motor.
2022-06-08 | Steam outage | NIST wide steam outage due to a leak. Hold off on testing until steam is back on line. Repaired 6/16/2022.
6/24/2022-6/26/2022 | Planned steam outage | Steam system down from afternoon of 6/24/2022 through 6/26/2022 for planned maintenance.
2022-09-19 | Steam valve leaking in OAU. Able to continue running.
2023-02-09 | Steam valve in OAU isn't responding | Reinstalled
2023-04-05 | Chiller1 is faulting | Cleaned the strainer in the evaporator, checked the subcool, cleaned contacts on the suction side pressure transducer. Seems to be okay for now, but monitoring the operation closely.
2023-10-02 | Chiller1 faulted | The chiller faulted because the pipe at the low side of the compressor cracked and refrigerant leaked out. Replaced compressor and VFD (10/30)
2023-11-06 | Embedded computer on the data rack has some sort of failure | Reformat the controller (11/6)

## ASHP
Date | Issue | Solution
2022-02-22 | damaged wire on the chiller motor starter | replacement
2022-02-23 | lack of deep learning toolboxes for airflow simulation | reinstall Matlab
2022-02-25 | Computer damaged by power bumps | Replace computer, reinstall software
2022-03-09 | had a failure of the reference junction on one of the TC cards | use existing RTD instead. Will verify RTD after replacing and recalibrating TC
3/9/2022-3/17/2022 | large emulation error | an additional steam injection is added to improve latent load control
2024-02-21 | there was an issue in supply air temperature, causing low COP. large emulation error early morning. MPC control may not be ideal due to its immediate implementation after being calculated. | Update the software code

## WSHP
Date | Issue | Solution
2022-01-06 | WSHP: occasional BACnet connection lost leading to us having to stop the test to restart LabVIEW in order to re-establish BACnet connection to the HP and WattNode. This issue has been rather random as we had one case that the connection broke after 30 min, while we have multiple 5hr+ tests without any issue. | Contact has been made to the NIST developer who provided the BACnet LabVIEW API to ask if similar behaviors have been reported and if there’s a corresponding fix. If no fix, recovery mode will be used.
2022-02-15 | OBM issue. Airflow model can't run. | Reinstall deep learning toolbox (2/16)
2022-02-28 | BACnet connection could not be established with the BCD library. Issue could be caused by updating to the latest version of LabVIEW. | 1. switch to commercial LabVIEW BACnet library (through VIPM) 2. roll back LabVIEW's version to similar to NIST systems (18' or 17')
2022-03-01 | B/IP library needs to set correct default network adapter (#1 instead of #0), currently WhoIs is not discovering any devices | contacted developer for tech support
2022-03-02 | B/IP library installed and proved working on single-point property reading, moving on to writing property and multiple-point I/O | re-installed LabVIEW missing previous libraries, working with IT to identify and reload them
2022-03-03 | missing FPGA compilation tool for LabVIEW | asked IT to install the library. implemented multi-point BACnet reading subVI.
2022-03-07 | B/IP library unable to write property to the heat pump | contacting the vendor for B/IP writing function, waiting for them to send us latest version. Exploring another BACnet library (Endigit) that has more recent releases
2022-03-08 | the latest version of B/IP library is installed, yet the writeProperty function is still not able to pass value to the heat pump | rolled back to LabVIEW 2019 and convert the project to the previous versions
2022-03-14 | new version of BCD proves to work with Mike's setup in NIST, thus the vi might work, and the problem might be with communication setup | try re-set the environment of the BCD
2022-03-17 | could not write to: Multistate Value for HP mode request (should use USIGNED_INT as type), and zone temperature (should use REAL as data type) | held a zoom call with BACnet library provider and troubleshoot the writing issue. Turns out the zone temperature value is somehow locked to a value with priority of 3, and only new values with priority of 2 or 1 can overwrite it. changed the related vi accordingly and the BACnet test vi is fully functional with both reading and writing
2022-03-22 | try to use existing vi developed for the BACnet library, need LabVIEW 2021 instead of 2019. | upgraded LabVIEW back to 2021 and installed necessary libraries in correct order. The LabVIEW-BACnet system is now fully operational
2022-03-23 | ready to resume normal test tomorrow
2022-03-28 | finished first full-day test, found following issues: 1, chilled water bypass valve was left open, HP water inlet was not controlled. 2, dehumidifier had an overflow, humidity ratio was poorly controlled from half way. | fix the listed issue and re-do the test tomorrow
2022-03-29 | heat pump compressor didn't start during overnight test | checked electrical hardware, compressor control voltage is successfully passed to the local control board. The compressor resumed working after controller cover was opened, could be losen wire but could not find any. going to power-cycle the heat pump and run another test to see if issue persists.
3/30/2022 - 4/1/2022 | failsafe triggered during overnight test due to water pressure loss in the load coil line | troubleshoot the load coil water loop
2022-04-14 | heat pump didn't start during shoulder season runs, need to investigate
2022-04-17 | heat pump compressor couldn't get into stable operation, have trouble turn on and produce cooling | contact Trane for troubleshooting
4/17-5/15 | heat pump compressor replacement
2022-05-18 | ran Atlanta Def, the humidity was not able to get lower than 9g/kg as the auxillary AC was not turned on to help dehumidify the air. The AC was kept off in the concern of insufficient air preheating with air heaters due to water heater failure. The air heaters turned out to be adequate when AC is turned on in the second half of the test. | run again with auxillary AC on